УДК

LOCATING A SINGLE-PHASE EARTH FAULTS IN NETWORKS WITH ISOLATED NEUTRAL

Gatina D.R.

Scientific advisor: Yu.V. Piskovatsky, associate professor

(Kazan State Power Engineering University)

The most frequent type of fault on transmission lines is the single-phase earth fault. Single-phase earth faults account for about 70-90% of all faults in power systems. The course of various physical processes caused by earth faults significantly depends on the mode of operation of the network neutral.

6-35 kV networks operate on isolated neutral or neutral earthed through a considerable additional resistance. The earth fault current will be small as there’s no closed circuit for current flow due to the insulation of the neutral. A single-phase ground fault is through the capacitances of the undamaged phases. This current is about 10-30 A, which is insignificant, and is determined by the capacitance of the undamaged phases.

In networks with insulated neutral points, a short-circuit fault can have such dangerous consequences as:

1.	Depending on the branching of the network, the capacitive current ranges from 0.1 to 500 A. This magnitude of current poses a danger to people who are near the fault, for which reason these faults must be identified and disconnected.

2.	A single-phase ground fault causes an arc fault. During an arc fault, overvoltages occur that are 2-4 times the phase voltage. The insulation can not withstand these overvoltages, so there is a risk of an insulation breakdown at any point in the network and an occurrence of double earth fault.

3.	During the process of development and liquidation of the phase-to-ground fault occurs a ferroresonance effect in voltage transformers, which leads to their premature failure [1].

It becomes clear that it is necessary to quickly determine the location of a single-phase earth fault and to disconnect the faulted element – this is the purpose of our research.

One way to do this is to determine the location of a single-phase earth fault by identifying the pole with an insulation fault.

How does it work? The device contains a pointer mounted on each pole with a transmitter. When the phase insulation of the pole is damaged, the pointer triggers the transmitter, which transmits the number of the damaged pole via the communication channel to the operating personnel at the receiver installed in the control room.

According to the proposed method, it is possible to determine the damaged line and pole, the distance to the fault location and to disconnect the damaged line with a time commensurate with several periods of the industrial frequency.

Thanks to this method, the time for determining the location of a single-phase earth fault is reduced and the material costs for fault location are reduced.

References:

1. Pooler, W.J.R.H. Electrical Power / W.J.R.H. Pooler. – London: Ventus Publishing, 2011. – 221 p.